## Sheet1
SPRING HANGERS

Spring Hanger Size and Series Selection

			How to use hanger selection table: In order to choose a proper size					The chart must be read opposite from the direction of the pipe’s
			hanger, it is necessary to know the actual load which the spring is to					movement. The load arrived at is the cold load.
			support and the amount and direction of the pipe line movement					If the cold load falls outside of the working load range of the hanger
	from the cold to the hot position.					selected, relocate the actual or hot load in the adjacent column and
			Find the actual load of the pipe in the load table. As it is desirable to					find the cold load. When the hot and cold loads are both within the
			support the actual weight of the pipe when the line is hot, the actual					working range of a hanger, the size number of that hanger will be
			load is the hot load. To determine the cold load, read the spring					found at the top of the column.
			scale, up or down, for the amount of expected movement.
					LOAD TABLE (LBS) FOR SELECTION OF HANGER SIZE (sizes 10 through 22 on next page)
		Working Range (in) unshaded					Hanger size
		Shaded Rows Show Overtravel
		Figure No.					B-268 Only					Fig. 82, Fig. B-268, Fig. 98, Triple & Quadruple Spring
Quad.	Triple	98	B-268	82		000	00	0	1	2	3	4	5	6	7	8	9
2	11⁄2	1	1⁄2	1⁄4		7	19	43	63	81	105	141	189	252	336	450	600
2	11⁄2	1	1⁄2	1⁄4		7	20	44	66	84	109	147	197	263	350	469	625
2	11⁄2	1	1⁄2	1⁄4		8	22	46	68	88	114	153	206	273	364	488	650
2	11⁄2	1	1⁄2	1⁄4		9	24	48	71	91	118	159	213	284	378	506	675
0	0	0	0	0		10	26	50	74	95	123	165	221	294	392	525	700
					11	28	52	76	98	127	170	228	305	406	544	725
					12	30	54	79	101	131	176	236	315	420	563	750
					12	31	56	81	105	136	182	244	326	434	581	775
2	11⁄2	1	1⁄2	1⁄4		14	34	58	84	108	140	188	252	336	448	600	800
					14	35	59	87	111	144	194	260	347	462	619	825
					15	38	61	89	115	149	200	268	357	476	638	850
					16	40	63	92	118	153	206	276	368	490	656	875
4	3	2	1	1⁄2		17	41	65	95	122	158	212	284	378	504	675	900
					18	43	67	97	125	162	217	291	389	518	694	925
					19	45	69	100	128	166	223	299	399	532	713	950
					20	47	71	102	132	171	229	307	410	546	731	975
6	41⁄2	3	11⁄2	3⁄4		21	49	73	105	135	175	235	315	420	560	750	1,000
					21	50	74	108	138	179	241	323	431	574	769	1,025
					22	53	76	110	142	184	247	331	441	588	788	1,050
					23	55	78	113	145	188	253	339	452	602	806	1,075
8	6	4	2	1		24	56	80	116	149	193	258	347	462	616	825	1,100
					25	58	82	118	152	197	264	354	473	630	844	1,125
					26	60	84	121	155	201	270	362	483	644	863	1,150
					27	62	86	123	159	206	276	370	494	658	881	1,175
10	71⁄2	5	21⁄2	1	1⁄4	28	64	88	126	162	210	282	378	504	672	900	1,200
2	11⁄2	1	1⁄2	1⁄4		28	66	89	129	165	214	288	386	515	686	919	1,225
2	11⁄2	1	1⁄2	1⁄4		29	68	91	131	169	219	294	394	525	700	938	1,250
2	11⁄2	1	1⁄2	1⁄4		30	70	93	134	172	223	300	402	536	714	956	1,275
2	11⁄2	1	1⁄2	1⁄4		31	72	95	137	176	228	306	410	546	728	975	1,300
					Spring Rate (lbs/In)
					82	-	-	30	42	54	70	94	126	168	224	300	400
					B-268	7	15	15	21	27	35	47	63	84	112	150	200
					98	-	-	7	10	13	17	23	31	42	56	75	100
					Triple	-	-	5	7	9	12	16	21	28	37	50	67
				Quadruple		-	-	4	5	7	9	12	16	21	28	38	50
		Note: General rule for series selection use Fig. 82 for up to					1⁄2" of movement up to 1" use Fig. B-268, up to 2" use Fig. 98, up to 3" use a Triple, up to 4" use a Quadruple.
		Double check to assure desired variability is achieved.
174					www.anvilintl.com
PH-11.11					For more information please visit www.anvileps.com/product/spring-hangers.com or contact eps_contact@anvilintl.com

SPRING HANGERS

Spring Hanger Size and Series Selection

			How to use hanger selection table (cont.): Should it be impossible to					Cold load = (hot load) ± (movement) x (spring rate)
			select a hanger in a particular series such that both loads occur within					A key criteria in selecting the size and series of a variable spring is a
			the working range, consideration should be given to a variable spring					factor known as variability. This is a measurement of the percentage
			hanger with a wider working range or a constant support hanger.					change in supporting force between the hot and cold positions of a
			The cold load is calculated by adding (for up movement) or					spring and is calculated from the formula:
			subtracting (for down movement) the product of spring rate times					Variability = (Movement) x (Spring Rate) / (Hot Load)
		movement to or from the hot load.					If an allowable variability is not specified, good practice would be to
					use 25% as recommended by MSS-SP-58.
					LOAD TABLE (LBS) FOR SELECTION OF HANGER SIZE (Continued from previous page)
					Hanger size					Working Range (in) unshaded
					Shaded Rows Show Overtravel
					Fig. 82, Fig. B-268, Fig. 98, Triple & Quadruple Spring					Figure No.
10	11	12	13	14	15	16	17	18	19	20	21	22	82		B-268	98	Triple	Quad.
780	1,020	1,350	1,800	2,400	3,240	4,500	6,000	7,990	10,610	14,100	18,750	25,005
813	1,063	1,406	1,875	2,500	3,375	4,688	6,250	8,322	11,053	14,588	19,531	26,047
845	1,105	1,463	1,950	2,600	3,510	4,875	6,500	8,655	11,495	15,275	20,313	27,089
878	1,148	1,519	2,025	2,700	3,645	5,063	6,750	8,987	11,938	15,863	21,094	28,131
910	1,190	1,575	2,100	2,800	3,780	5,250	7,000	9,320	12,380	16,450	21,875	29,173	0		0	0	0	0
943	1,233	1,631	2,175	2,900	3,915	5,438	7,250	9,652	12,823	17,038	22,656	30,215
975	1,275	1,688	2,250	3,000	4,050	5,625	7,500	9,985	13,265	17,625	23,438	31,256
1,008	1,318	1,744	2,325	3,100	4,185	5,813	7,750	10,317	13,708	18,213	24,219	32,298
1,040	1,360	1,800	2,400	3,200	4,320	6,000	8,000	10,650	14,150	18,800	25,000	33,340	1⁄4		1⁄2	1	11⁄2	2
1,073	1,403	1,856	2,475	3,300	4,455	6,188	8,250	10,982	14,592	19,388	25,781	34,382
1,105	1,445	1,913	2,550	3,400	4,590	6,375	8,500	11,315	15,035	19,975	26,563	35,424
1,138	1,488	1,969	2,625	3,500	4,725	6,563	8,750	11,647	15,477	20,563	27,344	36,466
1,170	1,530	2,025	2,700	3,600	4,860	6,750	9,000	11,980	15,920	21,150	28,125	37,508	1⁄2		1	2	3	4
1,203	1,573	2,081	2,775	3,700	4,995	6,938	9,250	12,312	16,362	21,738	28,906	38,549
1,235	1,615	2,138	2,850	3,800	5,130	7,125	9,500	12,645	16,805	22,325	29,688	39,591
1,268	1,658	2,194	2,925	3,900	5,265	7,313	9,750	12,977	17,247	22,913	30,469	40,633
1,300	1,700	2,250	3,000	4,000	5,400	7,500	10,000	13,310	17,690	23,500	31,250	41,675	3⁄4		11⁄2	3	41⁄2	6
1,333	1,743	2,306	3,075	4,100	5,535	7,688	10,250	13,642	18,132	24,088	32,031	42,717
1,365	1,785	2,363	3,150	4,200	5,670	7,875	10,500	13,975	18,575	24,675	32,813	43,759
1,398	1,828	2,419	3,225	4,300	5,805	8,063	10,750	14,307	19,017	25,263	33,594	44,801
1,430	1,870	2,475	3,300	4,400	5,940	8,250	11,000	14,640	19,460	25,850	34,375	45,843	1		2	4	6	8
1,463	1,913	2,531	3,375	4,500	6,075	8,438	11,250	14,972	19,902	26,438	35,156	46,885
1,495	1,955	2,588	3,450	4,600	6,210	8,625	11,500	15,305	20,345	27,025	35,938	47,926
1,528	1,998	2,644	3,525	4,700	6,345	8,813	11,750	15,637	20,787	27,613	36,719	48,968
1,560	2,040	2,700	3,600	4,800	6,480	9,000	12,000	15,970	21,230	28,200	37,500	50,010	1	1⁄4	21⁄2	5	71⁄2	10
1,593	2,083	2,756	3,675	4,900	6,615	9,188	12,250	16,302	21,672	28,788	38,281	51,052
1,625	2,125	2,813	3,750	5,000	6,750	9,375	12,500	16,635	22,115	29,375	39,063	52,094
1,658	2,168	2,869	3,825	5,100	6,885	9,563	12,750	16,967	22,557	29,963	39,844	53,136
1,690	2,210	2,925	3,900	5,200	7,020	9,750	13,000	17,300	23,000	30,550	40,625	54,178
					Spring Rate (lbs/In)
520	680	900	1,200	1,600	2,160	3,000	4,000	5,320	7,080	9,400	12,500	16,670	82
260	340	450	600	800	1,080	1,500	2,000	2,660	3,540	4,700	6,250	8,335	B-268
130	170	225	300	400	540	750	1,000	1,330	1,770	2,350	3,125	4,167	98
87	113	150	200	267	360	500	667	887	1,180	1,567	2,083	2,778	Triple
65	85	113	150	200	270	375	500	665	885	1,175	1,563	2,084		Quadruple
					Note: General rule for series selection use Fig. 82 for up to 1⁄2" of movement up to 1" use Fig. B-268, up to 2" use Fig. 98, up to 3" use a Triple, up to 4" use a Quadruple.
		Double check to assure desired variability is achieved.
				www.anvilintl.com					175
					For more information please visit www.anvileps.com/product/spring-hangers.com or contact eps_contact@anvilintl.com					PH-11.11

## Sheet2
Quad.	Triple	98	B-268	82	000	00	0	1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19	20	21	22
2	1 1⁄2	1	1⁄2	1⁄4	7	19	43	63	81	105	141	189	252	336	450	600	780	1020	1350	1800	2400	3240	4500	6000	7990	10610	14100	18750	25005
2	1 1⁄2	1	1⁄2	1⁄4	7	20	44	66	84	109	147	197	263	350	469	625	813	1063	1406	1875	2500	3375	4688	6250	8322	11053	14588	19531	26047
2	1 1⁄2	1	1⁄2	1⁄4	8	22	46	68	88	114	153	206	273	364	488	650	845	1105	1463	1950	2600	3510	4875	6500	8655	11495	15275	20313	27089
2	1 1⁄2	1	1⁄2	1⁄4	9	24	48	71	91	118	159	213	284	378	506	675	878	1148	1519	2025	2700	3645	5063	6750	8987	11938	15863	21094	28131
0	0	0	0	0	10	26	50	74	95	123	165	221	294	392	525	700	910	1190	1575	2100	2800	3780	5250	7000	9320	12380	16450	21875	29173
					11	28	52	76	98	127	170	228	305	406	544	725	943	1233	1631	2175	2900	3915	5438	7250	9652	12823	17038	22656	30215
					12	30	54	79	101	131	176	236	315	420	563	750	975	1275	1688	2250	3000	4050	5625	7500	9985	13265	17625	23438	31256
					12	31	56	81	105	136	182	244	326	434	581	775	1008	1318	1744	2325	3100	4185	5813	7750	10317	13708	18213	24219	32298
2	1 1⁄2	1	1⁄2	1⁄4	14	34	58	84	108	140	188	252	336	448	600	800	1040	1360	1800	2400	3200	4320	6000	8000	10650	14150	18800	25000	33340
					14	35	59	87	111	144	194	260	347	462	619	825	1073	1403	1856	2475	3300	4455	6188	8250	10982	14592	19388	25781	34382
					15	38	61	89	115	149	200	268	357	476	638	850	1105	1445	1913	2550	3400	4590	6375	8500	11315	15035	19975	26563	35424
					16	40	63	92	118	153	201	276	368	490	656	875	1138	1488	1969	2625	3500	4725	6563	8750	11647	15477	20563	27344	36466
4	3	2	1	1⁄2	17	41	65	95	122	158	202	284	378	504	675	900	1170	1530	2025	2700	3600	4860	6750	9000	11980	15920	21150	28125	37508
					18	43	67	97	125	162	203	291	389	518	694	925	1203	1573	2081	2775	3700	4995	6938	9250	12312	16362	21738	28906	38549
					19	45	69	100	128	166	204	299	399	532	713	950	1235	1615	2138	2850	3800	5130	7125	9500	12645	16805	22325	29688	39591
					20	47	71	102	132	171	205	307	410	546	731	975	1268	1658	2194	2925	3900	5265	7313	9750	12977	17247	22913	30469	40633
6	4 1⁄2	3	1 1⁄2	3⁄4	21	49	73	105	135	175	206	315	420	560	750	1000	1300	1700	2250	3000	4000	5400	7500	10000	13310	17690	23500	31250	41675
					21	50	74	108	138	179	207	323	431	574	769	1025	1333	1743	2306	3075	4100	5535	7688	10250	13642	18132	24088	32031	42717
					22	53	76	110	142	184	208	331	441	588	788	1050	1365	1785	2363	3150	4200	5670	7875	10500	13975	18575	24675	32813	43759
					23	55	78	113	145	188	209	339	452	602	806	1075	1398	1828	2419	3225	4300	5805	8063	10750	14307	19017	25263	33594	44801
8	6	4	2	1	24	56	80	116	149	193	210	347	462	616	825	1100	1430	1870	2475	3300	4400	5940	8250	11000	14640	19460	25850	34375	45843
					25	58	82	118	152	197	211	354	473	630	844	1125	1463	1913	2531	3375	4500	6075	8438	11250	14972	19902	26438	35156	46885
					26	60	84	121	155	201	212	362	483	644	863	1150	1495	1955	2588	3450	4600	6210	8625	11500	15305	20345	27025	35938	47926
					27	62	86	123	159	206	213	370	494	658	881	1175	1528	1998	2644	3525	4700	6345	8813	11750	15637	20787	27613	36719	48968
10	7 1⁄2	5	2 1⁄2	1 ¼	28	64	88	126	162	210	214	378	504	672	900	1200	1560	2040	2700	3600	4800	6480	9000	12000	15970	21230	28200	37500	50010
2	1 1⁄2	1	1⁄2	1⁄4	28	66	89	129	165	214	215	386	515	686	919	1225	1593	2083	2756	3675	4900	6615	9188	12250	16302	21672	28788	38281	51052
2	1 1⁄2	1	1⁄2	1⁄4	29	68	91	131	169	219	216	394	525	700	938	1250	1625	2125	2813	3750	5000	6750	9375	12500	16635	22115	29375	39063	52094
2	1 1⁄2	1	1⁄2	1⁄4	30	70	93	134	172	223	217	402	536	714	956	1275	1658	2168	2869	3825	5100	6885	9563	12750	16967	22557	29963	39844	53136
2	1 1⁄2	1	1⁄2	1⁄4	31	72	95	137	176	228	218	410	546	728	975	1300	1690	2210	2925	3900	5200	7020	9750	13000	17300	23000	30550	40625	54178

				82	-	-	30	42	54	70	94	126	168	224	300	400	520	680	900	1200	1600	2160	3000	4000	5320	7080	9400	12500	16670
				B-268	7	15	15	21	27	35	47	63	84	112	150	200	260	340	450	600	800	1080	1500	2000	2660	3540	4700	6250	8335
				98	-	-	7	10	13	17	23	31	42	56	75	100	130	170	225	300	400	540	750	1000	1330	1770	2350	3125	4167
				Triple	-	-	5	7	9	12	16	21	28	37	50	67	87	113	150	200	267	360	500	667	887	1180	1567	2083	2778
				Quad	-	-	4	5	7	9	12	16	21	28	38	50	65	85	113	150	200	270	375	500	665	885	1175	1563	2084